## Sheet1
Project Title: |  |  | Project No: |  |  | Work Package No:
20 Ton Units |  |  | V128 |  |  | V128-WDP-002
Client: |  |  | Job Site/Location: |  |  | Prepared By:
Bechtel |  |  | VIT |  |  | E. Slagle
Pneumatic Stored Energy (PSE) calculation to be utilized during safety review to establish limited access/safety boundaries during pnuematic testing activties.
Complete entries in provided fields below to calculate the free air volume for all piping to be pressurized during the testing activies. Calculation is determined by multipying the linear feet (lf) of pipe by the pipe inside area (ft3) for the pressurized pipe.
Establish required test pressure and free air volume in ft3, input the values in the following applicable fields to calculate the stored energy in foot pounds force (ft-lbsf).
Pneumatic Stored Energy equation: 2.5*V*[144*(P+14.7)]*[1-(14.7/P+14.7)0.286]
Input Data
|  | Pipe I.D. (In.) | 1.25 | Dia.
|  | Length (Lf.) | 100 | Lf.
|  | Volume (Ft3) | 8.1813 | Ft3
|  | Test Pressure (Psig) | 300 | Psig.
Results
|  | Test Pressure: | 300 | Psig. | Free Air Volume: | 8.1813 | Ft3
|  | Pneumatic Stored Energy = |  | -1074304.5276 |  | ft-lbf
NOTE: Where multiple test are to be performed, calculation may be based on largest pipe size along with longest run to establish limited access/safety boundary for all testing.
Recommended Limited Access/Safety Boundary
|  | Stored Energy |  |  | Limited Access/Safety Boundary
|  | Less than 9,588,801 ft-lbf |  |  | 25 ft
|  | 9,588,801 ft-lbf to 25,078,400 ft-lbf |  |  | 50 ft
|  | 25,078,400 ft-lbf to 199,152,000 ft-lbf |  |  | 150 ft
|  | Greater than 199,152,000 ft-lbf |  |  | 330 ft